## 1.Intro - Index
Questionnaire: HVDC Biscay Gulf Interconnection
Applicant: |  | please enter name of applicant
NOTE: The Applicant Name entered here shall autopopulate the rest of this document
INTRODUCTION & INDEX
| This File contains the following Sections: |  | Who Should Read
Section 1: Intro
| Section 2: Cable Sizing Case A |  | Cable supplier
Section 2.1: Test Certification and projects
Section 2.2: Risk analysis Case A
| Section 3: Cable Sizing Case B |  | Cable supplier
Section 3.1: Test Certification and projects
Section 3.2: Risk analysis Case B
| Section 4: Comparaison of Cases |  | Cable supplier
Closing date for submission of responses: 11 April 2018
Applicants are required to answer the questionnaire in a specific, clear and concise/succinct way which clearly demonstrates the Applicant's capabilities
(please do not include sales or marketing information / brochures).

## 2.Cable design - Solution A
Case A
Questionnaire: HVDC Biscay Gulf Interconnection
Applicant: | please enter name of applicant
Section 2: Cable Sizing Case A
Ref. | Topics | XLPE |  | MIND
|  | 320 kV | 400 kV | 500 kV
S.1 | Based on your calculations (thermal, mechanical) for case A according to Appendix 1, 3 and 4, please provide a cable design with an aluminium conductor. The characteristics shall be given according to the Appendix 4.
S.2 | Based on your calculations (thermal, mechanical) for case A according to Appendix 1, 3 and 4, please provide a cable design with an copper conductor. The characteristics shall be given according to the Appendix 4.
S.3 | Do you have experience in testing such cross section (Al and/or Cu)? If yes, please provide test credibility for equal or bigger cross section. | Report in 2.1 | Report in 2.1 | Report in 2.1
S.4 | Do you have experience in installing such cross section (Al and/or Cu)? If yes, please provide project references for equal or bigger cross section. | Report in 2.1 | Report in 2.1 | Report in 2.1

## 2.1.Test & Project - Case A
Case A
Section 2.1: Test Certification and projects
XLPE Pre-Qualification Testing
Reference of test report (certificate number) | DC Voltage | Cross Section Area & Material | HVDC submarine/land cable | Cable Accessory - Field joint | Cable Accessory - Transition Joint | Cable Accessory - Factory joint | standards applied
XLPE Type Testing
Reference of test report (certificate number) | DC Voltage | Cross Sectional Area | HVDC submarine cable | Cable Accessory - Field joint | Cable Accessory - Transition Joint (for Information only) | Cable Accessory - Factory joint | standards applied
HVDC XLPE project Experience
Project Name | Voltage | Project Completion Date | Cross Sectional Area & Material | Power Rating | Length of submarine XLPE cable manufactured and installed | Force during installation [KN] | Tension during installation
MIND Type Testing
Reference of test report (certificate number) | DC Voltage | Cross Sectional Area | HVDC submarine cable | Cable Accessory - Field joint | Cable Accessory - Transition Joint | Cable Accessory - Factory joint | standards applied
MIND project Experience
Project Name | Voltage | Project Completion Date | Cross Sectional Area & Material | Power Rating | Length of submarine MIND cable manufactured and installed | Force during installation [KN] | Tension during installation

## 2.2.Risk analysis - Case A
case A
Questionnaire: HVDC Biscay Gulf Interconnection |  | Risk level
Applicant: | please enter name of applicant | High
Medium
Section 2.2: Risk analysis Case A |  | Low
Ref. | Topics | 320 kV XLPE (answer) | Risk | Risk mitigation | 400 kV XLPE (answer) | Risk | Risk mitigation | 500 kV MIND (answer) | Risk | Risk mitigation
1 | Installation
1.1 | Please describe the procedure of installation of the cable systems in the HDD (boats, pulling method…) you would propose.
1.2 | During the pulling in the HDD, what will be: - The maximum tensile force [kN] on the cable system? - The maximum side wall pressure [kN/m] on the cable system? - The maximum longitudinal compression force [kN] on the cable system? - The maximum crush force [kN] on the cable system? How do you calculate those values? Provide the name of the tool/software.
1.3 | Have you ever tested (during a type test or a prequalification test) a cable system (cable + joints) with such forces? If yes, please provide test evidences. If no, do you see any risks? - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.4 | Have you already installed cable systems subject to such forces? If yes, please provide former experiences. If no, do you see any risks? - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.5 | If the forces on the cable system during installation are higher than the maximum forces already tested or installed, how have you designed the cable in order to withstand the required forces: - Design of the conductor? - Increase of the cross section? - Design of the armour? - Other modifications that you found relevant? Do you see any risk regarding the modification of cable design? If yes, - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.6 | If the forces on the cable system during installation are higher than the maximum forces already tested or installed, what would you recommend in terms of: - Position of the joints (repair or factory)? - Distance of those joints to the HDD? - Other aspects of the cable system configuration that you find relevant? Do you see any risk regarding those aspects? If yes, - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.7 | What is the recommanded ratio of the inner diameter of pipe/outer diameter of cable for your projects? If the forces on the cable system during installation are higher than the maximum forces already tested or installed, what would you recommend regarding HDD design and cable installation: - Increase of inner diameter of the pipe? - Coating of the inner surface of the pipe? - Increase of bending radius of the pipe? - Lubrication of the pipe during installation? - Other modifications that you find relevant? Do you see any risk regarding those aspects? If yes, - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.8 | Did you have any experience on HVDC submarine transition joints? If yes, - Please indicate the nature of the cable conductors and their cross sections? - How you manage the thrust overload coming from the cables? Do you see any risk regarding HVDC transition joints? If yes, - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.9 | Do you think that the dilatation of the cable conductor in HDD (snaking phenomena) could induce permanent efforts on the joints (FJ/RJ) placed in or nearby the HDD? If yes, - Assess the risk level. - How would you protect the joints against this force: o Outside of HDD: Omega of the cable during installation, increase of the distance of the joints to the HDD...? o Inside the HDD: do you know any dispositive to reduce the efforts? (like cable snaking next to joint chamber for onshore cable system)
1.10 | Do you recommend a filling of the HDD with grout ? If yes, please detail. If not, provide the reasons. Do you see any risks? If yes - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.11 | Do you have the ability/experience to pull the optical fiber cables bundled to the power cables in HDD? Do you see any risk related to this configuration during installation? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
1.12 | If you propose a power cable with integrated optic fibres, do you see any risk for the integrity of the fibres during installation? If yes, - what are the risks/ Assess the risk level. - what would be the risk mitigation measures
1.13 | Do you see any other issues related to the installation that you find relevant?
2 | Reliability of the cable system during operation
MIND Technology
2.1 | Is this technology compatible with an installation such as case A with HDD slope ≤ 15° and a maximum depth of HDD around 135 m (below sea level)? Do you see any risk related to this configuration during installation? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures? If the entry angle and/or slope are considered too high for this technolgoy. What would be the maximun you would allow?
2.2 | Do you consider any issues regarding the premature ageing of cable with HDD slope ≤ 15° : - Oil migration due to the thermomecanical cycles - Paper shear due to the expansion/contraction of cable - Other phenomena that you find relevant? If yes, - What are the risks? Assess the risk level. - Would you consider an alternative solution to MIND cable? Do you think that other technologies such as PPLP could be more adapted to this configuration? - Would you consider a change of the HDD profile (slope, depth)? - What would be the risk mitigation measures
2.3 | Do you consider any issues regarding the mechanical fatigue due to the free movement of the cable in the tube with HDD slope ≤ 15°? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.4 | Do you consider any issues on the cable if the pipe is filled with grout (such as radial compression force due to the dilation of the cable)? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.5 | Do you think that sharper slopes (>15°) could be considered for the HDD profile? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
XLPE Technology
2.6 | Is this technology compatible with an installation such as case A with HDD slope ≤ 15° and a maximum depth of HDD around 135 m (below sea level)? Do you see any risk related to this configuration during installation? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures? If the entry angle and/or slope are considered too high for this technolgoy. What would be the maximun you would allow?
2.7 | Do you consider any issue regarding the mechanical fatigue due to the free movement of the cable in the tube with HDD slope ≤ 15°? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.8 | Do you consider any issue on the cable if the pipe is filled with grout (such as radial compression force due to the dilation of the cable)? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.9 | Do think that sharper slopes (>15°) could be considered for the HDD profile? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
Optical fiber
2.10 | Could you propose any temperature monitoring in the HDD part? If yes, - What is the proposed technology (integrated, bundle or in the seperated tube?) - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.11 | According to the length of the submarin link, how the temperature monitoring could be manage? - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
General
2.12 | In case of soil erosion at the entrance of HDD (see Appendix 5), how would you protect the cable and the pipe? Do you see any other risks at the HDD/cable interfaces? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.13 | Do you see any other issues related to the cable system in operation that you find relevant?
3 | Maintenance
3.1 | In case of cable failure, - Is a fault location possible? - If yes, how fault location would be managed? Please describe the procedure/setup, particularly taking into account the limited accuracy of TDR method ?
3.2 | Regarding the pipe, do you think that it could be damaged: - During its lifetime? - During a cable fault? - If the cable is removed? To prevent these phonomena, would you adapt the pipe characteristics (risk mitigation)?
3.3 | Do you consider it feasible to re-use a pipe and install a spare length in it? If yes, please describe the procedure to replace a damaged cable with a spare.
3,4 | Do you foresee any issue regarding the "fouling phenomena" in an empty pipe which could lead to an impossibility to use the pipe after several years ? How could prevent this phenomena ?
3,5 | Do you see any other issues related to the cable system maintenance that you find relevant?

## 3.Cable design - Case B
Case B
Questionnaire: HVDC Biscay Gulf Interconnection
Applicant: | please enter name of applicant
Section 3: Cable Sizing Case B
Ref. | Topics | XLPE |  | MIND
|  | 320 kV | 400 kV | 500 kV
S.1 | Based on your calculations (thermal, mechanical) for case B according to Appendix 2, 3 and 4, please provide a cable design with an aluminium conductor. The characteristics shall be given according to the Appendix 4.
S.2 | Based on your calculations (thermal, mechanical) for case B according to Appendix 2, 3 and 4, please provide a cable design with an copper conductor. The characteristics shall be given according to the Appendix 4.
S.3 | Do you have experience in testing such cross section (Al and/or Cu)? If yes, please provide test credibility for equal or bigger cross section. | Report in 3.1 | Report in 3.1 | Report in 3.1
S.4 | Do you have experience in installing such cross section (Al and/or Cu)? If yes, please provide project references for equal or bigger cross section. | Report in 3.1 | Report in 3.1 | Report in 3.1

## 3.1.Test & Project - Case B
Case B
Section 3.1: Test Certification and projects
XLPE Pre-Qualification Testing
Reference of test report (certificate number) | DC Voltage | Cross Section Area & Material | HVDC submarine/land cable | Cable Accessory - Field joint | Cable Accessory - Transition Joint | Cable Accessory - Factory joint | standards applied
XLPE Type Testing
Reference of test report (certificate number) | DC Voltage | Cross Sectional Area | HVDC submarine cable | Cable Accessory - Field joint | Cable Accessory - Transition Joint (for Information only) | Cable Accessory - Factory joint | standards applied
HVDC XLPE project Experience
Project Name | Voltage | Project Completion Date | Cross Sectional Area & Material | Power Rating | Length of submarine XLPE cable manufactured and installed | Force during installation [KN] | Tension during installation
MIND Type Testing
Reference of test report (certificate number) | DC Voltage | Cross Sectional Area | HVDC submarine cable | Cable Accessory - Field joint | Cable Accessory - Transition Joint | Cable Accessory - Factory joint | standards applied
MIND project Experience
Project Name | Voltage | Project Completion Date | Cross Sectional Area & Material | Power Rating | Length of submarine MIND cable manufactured and installed | Force during installation [KN] | Tension during installation

## 3.2.Risk analysis - Case B
Case B
Questionnaire: HVDC Biscay Gulf Interconnection |  | Risk level
Applicant: | please enter name of applicant | High
Medium
Section 3.2: Risk analysis Case B |  | Low
Ref. | Topics | 320 kV XLPE (answer) | Risk | Risk mitigation | 400 kV XLPE (answer) | Risk | Risk mitigation | 500 kV MIND (answer) | Risk | Risk mitigation
1 | Installation
1.1 | Please describe the procedure of installation of the cable systems in the HDD (boats, pulling method…) you would propose.
1.2 | During the pulling in the HDD, what will be: - The maximum tensile force [kN] on the cable system? - The maximum sidewall pressure [kN/m] on the cable system? - The maximum longitudinal compression force [kN] on the cable system? - The maximum crush force [kN] on the cable system? How do you calculate those values? Provide the name of the tool/software.
1.3 | Have you ever tested (during a type test or a prequalification test) a cable system (cable + joints) with such forces? If yes, please provide test evidences. If no, do you see any risks? - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.4 | Have you already installed cable systems subject to such forces? If yes, please provide former experiences. If no, do you see any risks? - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.5 | Have you ever installed a cable system in a HDD at a landfall? Il yes, please describe the HDDs (length, depth, slopes…).
1.6 | If the forces on the cable system during installation are higher than the maximum forces already tested or installed, how have you designed the cable in order to withstand the required forces: - Design of the conductor? - Increase of the cross section? - Design of the armour? - Other modifications that you found relevant? Do you see any risk regarding the modification of cable design? If yes, - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.7 | If the forces on the cable system during installation are higher than the maximum forces already tested or installed, what would you recommend in terms of: - Position of the joints (repair or factory)? - Distance of those joints to the HDD? - Other aspects of the cable system configuration that you find relevant? Do you see any risk regarding those aspects? If yes, - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.8 | What is the recommanded ratio of the inner diameter of pipe/outer diameter of cable for your projects? If the forces on the cable system during installation are higher than the maximum forces already tested or installed, what would you recommend regarding HDD design and cable installation: - Increase of inner diameter of the pipe? - Coating of the inner surface of the pipe? - Increase of bending radius of the pipe? - Lubrication of the pipe during installation? - Other modifications that you find relevant? Do you see any risk regarding those aspects? If yes, - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.9 | Did you have any experience on HVDC submarine transition joints? If yes, - Please indicate the nature of the cable conductors and their cross sections? - How you manage the thrust overload coming from the cables? Do you see any risk regarding HVDC transition joints? If yes, - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.10 | Do you think that the dilatation of the cable conductor in HDD (snaking phenomena) could induce permanent efforts on the joints (FJ/RJ) placed in or nearby the HDD? If yes, - Assess the risk level. - How would you protect the joints against this force: o Outside of HDD: Omega of the cable during installation, increase of the distance of the joints to the HDD...? o Inside the HDD: do you know any dispositive to reduce the efforts? (like cable snaking next to joint chamber for onshore cable system)
1.11 | Do you recommend a filling of the HDD with grout ? If yes, please detail. If not, provide the reasons. Do you see any risks? If yes - Which ones? Assess the risk level. - What would be the risk mitigation measures?
1.12 | Do you have the ability/experience to pull optical fiber cables bundled to power cables in HDD? Do you see any risk related to this configuration during installation? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
1.13 | If you propose a power cable with integrated optic fibres, do you see any risk for the integrity of the fibres during installation? If yes, - what are the risks/ Assess the risk level. - what is the risk mitigation measures?
1.14 | Do you see any other issues related to the installation that you find relevant?
2 | Reliability of the cable system during operation
MIND Technology
2.1 | Is this technology compatible with an installation such as case B? Do you see any risk related to this configuration during installation? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures? If the entry angle and/or slope are considered too high for this technolgoy. What would be the maximun you would allow?
2.2 | Do you consider any issues regarding the premature ageing of cable: - Oil migration due to the thermomecanical cycles - Paper shear due to the expansion/contraction of cable - Other phenomena that you find relevant? If yes, - What are the risks? Assess the risk level. - Would you consider an alternative solution to MIND cable? Do you think that other technologies such as PPLP could be more adapted to this configuration? - Would you consider a change of the HDD profile (slope, depth)? - Do you see any other risk mitigations?
2.3 | Do you consider any issues regarding the mechanical fatigue due to the free movement of the cable in the tube? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.4 | Do you consider any issues on the cable if the pipe is filled with grout (such as radial compression force due to the dilation of the cable)? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.5 | Do think that sharper slopes could be considered for the HDD profile? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
XLPE Technology
2.6 | Is this technology compatible with an installation such as case B? Do you see any risk related to this configuration during installation? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures? If the entry angle and/or slope are considered too high for this technolgoy. What would be the maximun you would allow?
2.7 | Do you consider any issue regarding the mechanical fatigue due to the free movement of the cable in the tube? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.8 | Do you consider any issue on the cable if the pipe is filled with grout (such as radial compression force due to the dilation of the cable)? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.9 | Do you think that sharper slopes could be considered for the HDD profile? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
Optical fiber
2.10 | Could you propose any temperature monitoring in the HDD part? If yes, - What is the proposed technology (integrated, bundle or in the seperated tube?) - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.11 | According to the length of the submarin link, how the temperature monitoring could be manage? - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
General
2.12 | In case of soil erosion at the entrance of HDD (see Appendix 4), how would you protect the cable and the pipe? Do you see any other risks at the HDD/cable interfaces? If yes, - What are the risks? Assess the risk level. - What would be the risk mitigation measures?
2.13 | Do you see any other issues related to the cable system in operation that you find relevant?
3 | Maintenance
3.1 | In case of cable failure, - Is a fault location possible? - If yes, how fault location would be managed? Please describe the procedure/setup, particularly taking into account the limited accuracy of TDR method ?
3.2 | Regarding the pipe, do you think that it could be damaged: - During its lifetime? - During a cable fault? - If the cable is removed? To prevent these phonomena, would you adapt the pipe characteristics (risk mitigation)?
3.3 | Do you consider it feasible to re-use a pipe and install a spare length in it? If yes, please describe the procedure to replace a damaged cable with a spare.
3,4 | Do you foresee any issue regarding the "fouling phenomena" in an empty pipe which could lead to an impossibility to use the pipe after several years ? How could prevent this phenomena ?
3,5 | Do you see any other issues related to the cable system maintenance that you find relevant?
Note on C9: Argüelles Enjuanes, José Manuel: soluiton B is for MIND

## 3. Comparaison of solutions
Questionnaire: HVDC Biscay Gulf Interconnection
The answer for 400 XLPE need to be extrapolated from the 320 kV sizing.
*TT and PQ ( only for XLPE) have been passed succesfully.
| Topics | 320 kV XLPE | 400 kV XLPE | 500 kV MIND
Qualified technology and proposed by cable supplier *
Solution A | HDD ≤ 15°
Risk level related to the technology
Risk mitigations
HDD >15 °
Risk level related to the technology
Risk mitigations
Solution B | Risk level related to the technology
Risk mitigations